## Tag Mapping
TagName | DeviceName | ObjectType | Address | Bit | DataType | R_W | Scale | Offset | Unit | Poll_ms | Min | Max | Endian | Description | AlarmEnable | Deadband | WriteConfirm | SpareFlag
I545PD1500A | 545ME201CG1 | HR | 1 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 0.000 | 0.500 | ABCD | STR A DIFF PRESSURE IN | N |  | N | N
I545T4500A | 545ME201CG1 | HR | 3 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 0.0 | 100.0 | ABCD | STR A TEMP- ERATURE IN | N |  | N | N
I545P3500A | 545ME201CG1 | HR | 5 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 0.00 | 80.00 | ABCD | STR A PRESSURE IN | N |  | N | N
I545D1501A | 545ME201CG1 | HR | 7 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 | 0.0 | 491.0 | ABCD | STR A FT DENS IN | N |  | N | N
I545FCV1502A | 545ME201CG1 | HR | 9 |  | FLOAT32 | R | 1 | 0 | % | 1000 | 0.0 | 100.0 | ABCD | STR A FCV POSITION FB | N |  | N | N
I545F1501AA | 545ME201CG1 | HR | 11 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 | 0 | 1622 | ABCD | STR A GUVOL FR IN | N |  | N | N
I545F1501AB | 545ME201CG1 | HR | 13 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL FR IN | N |  | N | N
I545F1501AC | 545ME201CG1 | HR | 15 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR A MASS FR IN | N |  | N | N
I545F1501AD | 545ME201CG1 | HR | 17 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A METER DENS IN | N |  | N | N
I545F1501AE | 545ME201CG1 | HR | 19 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BASE DENS IN | N |  | N | N
I545F1501AF | 545ME201CG1 | HR | 21 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A K-FACTOR IN | N |  | N | N
I545F1501AG | 545ME201CG1 | HR | 23 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A M-FACTOR IN | N |  | N | N
I545F1501AH | 545ME201CG1 | HR | 25 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF IN | N |  | N | N
I545PD1500AC1 | 545ME201CG1 | HR | 27 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT CUR HOUR FWA | N |  | N | N
I545PD1500AC2 | 545ME201CG1 | HR | 29 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT CUR DAY FWA | N |  | N | N
I545PD1500AC3 | 545ME201CG1 | HR | 31 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT CUR MNTH FWA | N |  | N | N
I545P3500AC1 | 545ME201CG1 | HR | 33 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT CUR HOUR FWA | N |  | N | N
I545P3500AC2 | 545ME201CG1 | HR | 35 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT CUR DAY FWA | N |  | N | N
I545P3500AC3 | 545ME201CG1 | HR | 37 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT CUR MNTH FWA | N |  | N | N
I545T4500AC1 | 545ME201CG1 | HR | 39 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT CUR HOUR FWA | N |  | N | N
I545T4500AC2 | 545ME201CG1 | HR | 41 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT CUR DAY FWA | N |  | N | N
I545T4500AC3 | 545ME201CG1 | HR | 43 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT CUR MNTH FWA | N |  | N | N
I545F1501AAC1 | 545ME201CG1 | HR | 45 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS CUR HOUR FWA | N |  | N | N
I545F1501AAC2 | 545ME201CG1 | HR | 47 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS CUR DAY FWA | N |  | N | N
I545F1501AAC3 | 545ME201CG1 | HR | 49 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS CUR MNTH FWA | N |  | N | N
I545F1501ABC1 | 545ME201CG1 | HR | 51 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS CUR HOUR FWA | N |  | N | N
I545F1501ABC2 | 545ME201CG1 | HR | 53 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS CUR DAY FWA | N |  | N | N
I545F1501ABC3 | 545ME201CG1 | HR | 55 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS CUR MNTH FWA | N |  | N | N
I545F1501ACC1 | 545ME201CG1 | HR | 57 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF CUR HOUR FWA | N |  | N | N
I545F1501ACC2 | 545ME201CG1 | HR | 59 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF CUR DAY FWA | N |  | N | N
I545F1501ACC3 | 545ME201CG1 | HR | 61 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF CUR MNTH FWA | N |  | N | N
I545F1501ADC1 | 545ME201CG1 | HR | 63 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF CUR HOUR FWA | N |  | N | N
I545F1501ADC2 | 545ME201CG1 | HR | 65 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF CUR DAY FWA | N |  | N | N
I545F1501ADC3 | 545ME201CG1 | HR | 67 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF CUR MNTH FWA | N |  | N | N
I545F1501AEC1 | 545ME201CG1 | HR | 69 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF CUR HOUR FWA | N |  | N | N
I545F1501AEC2 | 545ME201CG1 | HR | 71 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF CUR DAY FWA | N |  | N | N
I545F1501AEC3 | 545ME201CG1 | HR | 73 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF CUR MNTH FWA | N |  | N | N
I545PD1500AP1 | 545ME201CG1 | HR | 75 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT PRE HOUR FWA | N |  | N | N
I545PD1500AP2 | 545ME201CG1 | HR | 77 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT PRE DAY FWA | N |  | N | N
I545PD1500AP3 | 545ME201CG1 | HR | 79 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT PRE MNTH FWA | N |  | N | N
I545P3500AP1 | 545ME201CG1 | HR | 81 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT PRE HOUR FWA | N |  | N | N
I545P3500AP2 | 545ME201CG1 | HR | 83 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT PRE DAY FWA | N |  | N | N
I545P3500AP3 | 545ME201CG1 | HR | 85 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT PRE MNTH FWA | N |  | N | N
I545T4500AP1 | 545ME201CG1 | HR | 87 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT PRE HOUR FWA | N |  | N | N
I545T4500AP2 | 545ME201CG1 | HR | 89 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT PRE DAY FWA | N |  | N | N
I545T4500AP3 | 545ME201CG1 | HR | 91 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT PRE MNTH FWA | N |  | N | N
I545F1501AAP1 | 545ME201CG1 | HR | 93 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS PRE HOUR FWA | N |  | N | N
I545F1501AAP2 | 545ME201CG1 | HR | 95 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS PRE DAY FWA | N |  | N | N
I545F1501AAP3 | 545ME201CG1 | HR | 97 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A BDNS PRE MNTH FWA | N |  | N | N
I545F1501ABP1 | 545ME201CG1 | HR | 99 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS PRE HOUR FWA | N |  | N | N
I545F1501ABP2 | 545ME201CG1 | HR | 101 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS PRE DAY FWA | N |  | N | N
I545F1501ABP3 | 545ME201CG1 | HR | 103 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR A MDNS PRE MNTH FWA | N |  | N | N
I545F1501ACP1 | 545ME201CG1 | HR | 105 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF PRE HOUR FWA | N |  | N | N
I545F1501ACP2 | 545ME201CG1 | HR | 107 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF PRE DAY FWA | N |  | N | N
I545F1501ACP3 | 545ME201CG1 | HR | 109 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A KF PRE MNTH FWA | N |  | N | N
I545F1501ADP1 | 545ME201CG1 | HR | 111 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF PRE HOUR FWA | N |  | N | N
I545F1501ADP2 | 545ME201CG1 | HR | 113 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF PRE DAY FWA | N |  | N | N
I545F1501ADP3 | 545ME201CG1 | HR | 115 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A MF PRE MNTH FWA | N |  | N | N
I545F1501AEP1 | 545ME201CG1 | HR | 117 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF PRE HOUR FWA | N |  | N | N
I545F1501AEP2 | 545ME201CG1 | HR | 119 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF PRE DAY FWA | N |  | N | N
I545F1501AEP3 | 545ME201CG1 | HR | 121 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A CCF PRE MNTH FWA | N |  | N | N
I545F1501ATC | 545ME201CG2 | HR | 123 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL CUMTOT | N |  | N | N
I545F1501AT1 | 545ME201CG2 | HR | 127 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL CUR HOUR TOT | N |  | N | N
I545F1501AT2 | 545ME201CG2 | HR | 131 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL CUR DAY TOT | N |  | N | N
I545F1501AT3 | 545ME201CG2 | HR | 135 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL CUR MNTH TOT | N |  | N | N
I545F1501AT4 | 545ME201CG2 | HR | 139 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL PRE HOUR TOT | N |  | N | N
I545F1501AT5 | 545ME201CG2 | HR | 143 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL PRE DAY TOT | N |  | N | N
I545F1501AT6 | 545ME201CG2 | HR | 147 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR A GUVOL PRE MNTH TOT | N |  | N | N
I545F1501ABTC | 545ME201CG2 | HR | 151 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL CUMTOT | N |  | N | N
I545F1501ABT1 | 545ME201CG2 | HR | 155 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL CUR HOUR TOT | N |  | N | N
I545F1501ABT2 | 545ME201CG2 | HR | 159 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL CUR DAY TOT | N |  | N | N
I545F1501ABT3 | 545ME201CG2 | HR | 163 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL CUR MNTH TOT | N |  | N | N
I545F1501ABT4 | 545ME201CG2 | HR | 167 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL PRE HOUR TOT | N |  | N | N
I545F1501ABT5 | 545ME201CG2 | HR | 171 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL PRE DAY TOT | N |  | N | N
I545F1501ABT6 | 545ME201CG2 | HR | 175 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL PRE MNTH TOT | N |  | N | N
I545F1501ACTC | 545ME201CG2 | HR | 179 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS CUMTOT | N |  | N | N
I545F1501ACT1 | 545ME201CG2 | HR | 183 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS CUR HOUR TOT | N |  | N | N
I545F1501ACT2 | 545ME201CG2 | HR | 187 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS CUR DAY TOT | N |  | N | N
I545F1501ACT3 | 545ME201CG2 | HR | 191 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS CUR MNTH TOT | N |  | N | N
I545F1501ACT4 | 545ME201CG2 | HR | 195 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS PRE HOUR TOT | N |  | N | N
I545F1501ACT5 | 545ME201CG2 | HR | 199 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS PRE DAY TOT | N |  | N | N
I545F1501ACT6 | 545ME201CG2 | HR | 203 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR A MASS PRE MNTH TOT | N |  | N | N
I545PD3504B | 545ME201CG3 | HR | 207 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 0.000 | 0.500 | ABCD | STR B DIFF PRESSURE IN | N |  | N | N
I545T4500B | 545ME201CG3 | HR | 209 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 0.0 | 100.0 | ABCD | STR B TEMP- ERATURE IN | N |  | N | N
I545P3500B | 545ME201CG3 | HR | 211 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 0.00 | 80.00 | ABCD | STR B PRESSURE IN | N |  | N | N
I545D1501B | 545ME201CG3 | HR | 213 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 | 0.0 | 491.0 | ABCD | STR B FT DENS IN | N |  | N | N
I545FCV1502B | 545ME201CG3 | HR | 215 |  | FLOAT32 | R | 1 | 0 | % | 1000 | 0.0 | 100.0 | ABCD | STR B FCV POSITION FB | N |  | N | N
I545F1501BA | 545ME201CG3 | HR | 217 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 | 0 | 1622 | ABCD | STR B GUVOL FR IN | N |  | N | N
I545F1501BB | 545ME201CG3 | HR | 219 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL FR IN | N |  | N | N
I545F1501BC | 545ME201CG3 | HR | 221 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR B MASS FR IN | N |  | N | N
I545F1501BD | 545ME201CG3 | HR | 223 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B METER DENS IN | N |  | N | N
I545F1501BE | 545ME201CG3 | HR | 225 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BASE DENS IN | N |  | N | N
I545F1501BF | 545ME201CG3 | HR | 227 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B K-FACTOR IN | N |  | N | N
I545F1501BG | 545ME201CG3 | HR | 229 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B M-FACTOR IN | N |  | N | N
I545F1501BH | 545ME201CG3 | HR | 231 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF IN | N |  | N | N
I545PD3504BC1 | 545ME201CG3 | HR | 233 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT CUR HOUR FWA | N |  | N | N
I545PD3504BC2 | 545ME201CG3 | HR | 235 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT CUR DAY FWA | N |  | N | N
I545PD3504BC3 | 545ME201CG3 | HR | 237 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT CUR MNTH FWA | N |  | N | N
I545P3500BC1 | 545ME201CG3 | HR | 239 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT CUR HOUR FWA | N |  | N | N
I545P3500BC2 | 545ME201CG3 | HR | 241 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT CUR DAY FWA | N |  | N | N
I545P3500BC3 | 545ME201CG3 | HR | 243 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT CUR MNTH FWA | N |  | N | N
I545T4500BC1 | 545ME201CG3 | HR | 245 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT CUR HOUR FWA | N |  | N | N
I545T4500BC2 | 545ME201CG3 | HR | 247 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT CUR DAY FWA | N |  | N | N
I545T4500BC3 | 545ME201CG3 | HR | 249 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT CUR MNTH FWA | N |  | N | N
I545F1501BAC1 | 545ME201CG3 | HR | 251 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS CUR HOUR FWA | N |  | N | N
I545F1501BAC2 | 545ME201CG3 | HR | 253 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS CUR DAY FWA | N |  | N | N
I545F1501BAC3 | 545ME201CG3 | HR | 255 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS CUR MNTH FWA | N |  | N | N
I545F1501BBC1 | 545ME201CG3 | HR | 257 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS CUR HOUR FWA | N |  | N | N
I545F1501BBC2 | 545ME201CG3 | HR | 259 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS CUR DAY FWA | N |  | N | N
I545F1501BBC3 | 545ME201CG3 | HR | 261 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS CUR MNTH FWA | N |  | N | N
I545F1501BCC1 | 545ME201CG3 | HR | 263 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF CUR HOUR FWA | N |  | N | N
I545F1501BCC2 | 545ME201CG3 | HR | 265 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF CUR DAY FWA | N |  | N | N
I545F1501BCC3 | 545ME201CG3 | HR | 267 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF CUR MNTH FWA | N |  | N | N
I545F1501BDC1 | 545ME201CG3 | HR | 269 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF CUR HOUR FWA | N |  | N | N
I545F1501BDC2 | 545ME201CG3 | HR | 271 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF CUR DAY FWA | N |  | N | N
I545F1501BDC3 | 545ME201CG3 | HR | 273 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF CUR MNTH FWA | N |  | N | N
I545F1501BEC1 | 545ME201CG3 | HR | 275 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF CUR HOUR FWA | N |  | N | N
I545F1501BEC2 | 545ME201CG3 | HR | 277 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF CUR DAY FWA | N |  | N | N
I545F1501BEC3 | 545ME201CG3 | HR | 279 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF CUR MNTH FWA | N |  | N | N
I545PD3504BP1 | 545ME201CG3 | HR | 281 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT PRE HOUR FWA | N |  | N | N
I545PD3504BP2 | 545ME201CG3 | HR | 283 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT PRE DAY FWA | N |  | N | N
I545PD3504BP3 | 545ME201CG3 | HR | 285 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT PRE MNTH FWA | N |  | N | N
I545P3500BP1 | 545ME201CG3 | HR | 287 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT PRE HOUR FWA | N |  | N | N
I545P3500BP2 | 545ME201CG3 | HR | 289 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT PRE DAY FWA | N |  | N | N
I545P3500BP3 | 545ME201CG3 | HR | 291 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT PRE MNTH FWA | N |  | N | N
I545T4500BP1 | 545ME201CG3 | HR | 293 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT PRE HOUR FWA | N |  | N | N
I545T4500BP2 | 545ME201CG3 | HR | 295 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT PRE DAY FWA | N |  | N | N
I545T4500BP3 | 545ME201CG3 | HR | 297 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT PRE MNTH FWA | N |  | N | N
I545F1501BAP1 | 545ME201CG3 | HR | 299 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS PRE HOUR FWA | N |  | N | N
I545F1501BAP2 | 545ME201CG3 | HR | 301 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS PRE DAY FWA | N |  | N | N
I545F1501BAP3 | 545ME201CG3 | HR | 303 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B BDNS PRE MNTH FWA | N |  | N | N
I545F1501BBP1 | 545ME201CG3 | HR | 305 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS PRE HOUR FWA | N |  | N | N
I545F1501BBP2 | 545ME201CG3 | HR | 307 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS PRE DAY FWA | N |  | N | N
I545F1501BBP3 | 545ME201CG3 | HR | 309 |  | FLOAT32 | R | 1 | 0 | kg/m3 | 1000 |  |  | ABCD | STR B MDNS PRE MNTH FWA | N |  | N | N
I545F1501BCP1 | 545ME201CG3 | HR | 311 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF PRE HOUR FWA | N |  | N | N
I545F1501BCP2 | 545ME201CG3 | HR | 313 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF PRE DAY FWA | N |  | N | N
I545F1501BCP3 | 545ME201CG3 | HR | 315 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B KF PRE MNTH FWA | N |  | N | N
I545F1501BDP1 | 545ME201CG3 | HR | 317 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF PRE HOUR FWA | N |  | N | N
I545F1501BDP2 | 545ME201CG3 | HR | 319 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF PRE DAY FWA | N |  | N | N
I545F1501BDP3 | 545ME201CG3 | HR | 321 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B MF PRE MNTH FWA | N |  | N | N
I545F1501BEP1 | 545ME201CG3 | HR | 323 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF PRE HOUR FWA | N |  | N | N
I545F1501BEP2 | 545ME201CG3 | HR | 325 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF PRE DAY FWA | N |  | N | N
I545F1501BEP3 | 545ME201CG3 | HR | 327 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B CCF PRE MNTH FWA | N |  | N | N
I545F1501BTC | 545ME201CG4 | HR | 329 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL CUMTOT | N |  | N | N
I545F1501BT1 | 545ME201CG4 | HR | 333 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL CUR HOUR TOT | N |  | N | N
I545F1501BT2 | 545ME201CG4 | HR | 337 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL CUR DAY TOT | N |  | N | N
I545F1501BT3 | 545ME201CG4 | HR | 341 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL CUR MNTH TOT | N |  | N | N
I545F1501BT4 | 545ME201CG4 | HR | 345 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL PRE HOUR TOT | N |  | N | N
I545F1501BT5 | 545ME201CG4 | HR | 349 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL PRE DAY TOT | N |  | N | N
I545F1501BT6 | 545ME201CG4 | HR | 353 |  | FLOAT64 | R | 1 | 0 | m3 | 1000 |  |  | ABCD | STR B GUVOL PRE MNTH TOT | N |  | N | N
I545F1501BBTC | 545ME201CG4 | HR | 357 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL CUMTOT | N |  | N | N
I545F1501BBT1 | 545ME201CG4 | HR | 361 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL CUR HOUR TOT | N |  | N | N
I545F1501BBT2 | 545ME201CG4 | HR | 365 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL CUR DAY TOT | N |  | N | N
I545F1501BBT3 | 545ME201CG4 | HR | 369 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL CUR MNTH TOT | N |  | N | N
I545F1501BBT4 | 545ME201CG4 | HR | 373 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL PRE HOUR TOT | N |  | N | N
I545F1501BBT5 | 545ME201CG4 | HR | 377 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL PRE DAY TOT | N |  | N | N
I545F1501BBT6 | 545ME201CG4 | HR | 381 |  | FLOAT64 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL PRE MNTH TOT | N |  | N | N
I545F1501BCTC | 545ME201CG4 | HR | 385 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS CUMTOT | N |  | N | N
I545F1501BCT1 | 545ME201CG4 | HR | 389 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS CUR HOUR TOT | N |  | N | N
I545F1501BCT2 | 545ME201CG4 | HR | 393 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS CUR DAY TOT | N |  | N | N
I545F1501BCT3 | 545ME201CG4 | HR | 397 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS CUR MNTH TOT | N |  | N | N
I545F1501BCT4 | 545ME201CG4 | HR | 401 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS PRE HOUR TOT | N |  | N | N
I545F1501BCT5 | 545ME201CG4 | HR | 405 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS PRE DAY TOT | N |  | N | N
I545F1501BCT6 | 545ME201CG4 | HR | 409 |  | FLOAT64 | R | 1 | 0 | ton | 1000 |  |  | ABCD | STR B MASS PRE MNTH TOT | N |  | N | N
I545A5500BN2 | 545ME201CG5 | HR | 413 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N2 IN | N |  | N | N
I545A5500BCO2 | 545ME201CG5 | HR | 415 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC CO2 IN | N |  | N | N
I545A5500BC1 | 545ME201CG5 | HR | 417 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC METHANE IN | N |  | N | N
I545A5500BC2 | 545ME201CG5 | HR | 419 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC ETHANE IN | N |  | N | N
I545A5500BC3 | 545ME201CG5 | HR | 421 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC PROPANE IN | N |  | N | N
I545A5500BIC4 | 545ME201CG5 | HR | 423 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC I-BUTANE IN | N |  | N | N
I545A5500BNC4 | 545ME201CG5 | HR | 425 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N-BUTANE IN | N |  | N | N
I545A5500BIC5 | 545ME201CG5 | HR | 427 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC I-PENTANEIN | N |  | N | N
I545A5500BNC5 | 545ME201CG5 | HR | 429 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N-PENTANEIN | N |  | N | N
I545A5500BC6 | 545ME201CG5 | HR | 431 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC HEXANE IN | N |  | N | N
I545A5500BC7 | 545ME201CG5 | HR | 433 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC HEPTANE IN | N |  | N | N
I545A5500BC8 | 545ME201CG5 | HR | 435 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC OCTANE IN | N |  | N | N
I545A5500BC9 | 545ME201CG5 | HR | 437 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC NONANE IN | N |  | N | N
I545A5500BC10 | 545ME201CG5 | HR | 439 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC DECANE IN | N |  | N | N
I545A5500BN2K | 545ME201CG6 | HR | 441 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N2 KP | N |  | N | N
I545A5500BCO2K | 545ME201CG6 | HR | 443 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC CO2 KP | N |  | N | N
I545A5500BC1K | 545ME201CG6 | HR | 445 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC METHANE KP | N |  | N | N
I545A5500BC2K | 545ME201CG6 | HR | 447 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC ETHANE KP | N |  | N | N
I545A5500BC3K | 545ME201CG6 | HR | 449 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC PROPANE KP | N |  | N | N
I545A5500BIC4K | 545ME201CG6 | HR | 451 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC I-BUTANE KP | N |  | N | N
I545A5500BNC4K | 545ME201CG6 | HR | 453 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N-BUTANE KP | N |  | N | N
I545A5500BIC5K | 545ME201CG6 | HR | 455 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC I-PENTANEKP | N |  | N | N
I545A5500BNC5K | 545ME201CG6 | HR | 457 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC N-PENTANEKP | N |  | N | N
I545A5500BC6K | 545ME201CG6 | HR | 459 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC HEXANE KP | N |  | N | N
I545A5500BC7K | 545ME201CG6 | HR | 461 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC HEPTANE KP | N |  | N | N
I545A5500BC8K | 545ME201CG6 | HR | 463 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC OCTANE KP | N |  | N | N
I545A5500BC9K | 545ME201CG6 | HR | 465 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC NONANE KP | N |  | N | N
I545A5500BC10K | 545ME201CG6 | HR | 467 |  | FLOAT32 | R | 1 | 0 | mol% | 1000 |  |  | ABCD | GC DECANE KP | N |  | N | N
I545PD1500ALI | 545ME201CG7 | HR | 469 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT LOW LIM | N |  | N | N
I545PD1500AHI | 545ME201CG7 | HR | 471 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT HIGH LIM | N |  | N | N
I545T4500ALI | 545ME201CG7 | HR | 473 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 11.90 | 16.20 | ABCD | STR A TT LOW LIM | N |  | N | N
I545T4500AHI | 545ME201CG7 | HR | 475 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 11.90 | 16.20 | ABCD | STR A TT HIGH LIM | N |  | N | N
I545P3500ALI | 545ME201CG7 | HR | 477 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 40.40 | 40.40 | ABCD | STR A PT LOW LIM | N |  | N | N
I545P3500AHI | 545ME201CG7 | HR | 479 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 40.40 | 40.40 | ABCD | STR A PT HIGH LIM | N |  | N | N
I545F1501AALI | 545ME201CG7 | HR | 481 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 |  |  | ABCD | STR A GUVOL LOW LIM | N |  | N | N
I545F1501AAHI | 545ME201CG7 | HR | 483 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 |  |  | ABCD | STR A GUVOL HIGH LIM | N |  | N | N
I545F1501ABLI | 545ME201CG7 | HR | 485 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL LOW LIM | N |  | N | N
I545F1501ABHI | 545ME201CG7 | HR | 487 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A GSVOL HIGH LIM | N |  | N | N
I545F1501ACLI | 545ME201CG7 | HR | 489 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR A MASS LOW LIM | N |  | N | N
I545F1501ACHI | 545ME201CG7 | HR | 491 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR A MASS HIGH LIM | N |  | N | N
I545PD1500AK | 545ME201CG7 | HR | 493 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A DPT KP | N |  | N | N
I545T4500AK | 545ME201CG7 | HR | 495 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR A TT KP | N |  | N | N
I545P3500AK | 545ME201CG7 | HR | 497 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR A PT KP | N |  | N | N
I545PD3504BLI | 545ME201CG7 | HR | 499 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT LOW LIM | N |  | N | N
I545PD3504BHI | 545ME201CG7 | HR | 501 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT HIGH LIM | N |  | N | N
I545T4500BLI | 545ME201CG7 | HR | 503 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 11.90 | 16.20 | ABCD | STR B TT LOW LIM | N |  | N | N
I545T4500BHI | 545ME201CG7 | HR | 505 |  | FLOAT32 | R | 1 | 0 | °C | 1000 | 11.90 | 16.20 | ABCD | STR B TT HIGH LIM | N |  | N | N
I545P3500BLI | 545ME201CG7 | HR | 507 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 40.40 | 40.40 | ABCD | STR B PT LOW LIM | N |  | N | N
I545P3500BHI | 545ME201CG7 | HR | 509 |  | FLOAT32 | R | 1 | 0 | barg | 1000 | 40.40 | 40.40 | ABCD | STR B PT HIGH LIM | N |  | N | N
I545F1501BALI | 545ME201CG7 | HR | 511 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 |  |  | ABCD | STR B GUVOL LOW LIM | N |  | N | N
I545F1501BAHI | 545ME201CG7 | HR | 513 |  | FLOAT32 | R | 1 | 0 | m3/H | 1000 |  |  | ABCD | STR B GUVOL HIGH LIM | N |  | N | N
I545F1501BBLI | 545ME201CG7 | HR | 515 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL LOW LIM | N |  | N | N
I545F1501BBHI | 545ME201CG7 | HR | 517 |  | FLOAT32 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B GSVOL HIGH LIM | N |  | N | N
I545F1501BCLI | 545ME201CG7 | HR | 519 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR B MASS LOW LIM | N |  | N | N
I545F1501BCHI | 545ME201CG7 | HR | 521 |  | FLOAT32 | R | 1 | 0 | ton/H | 1000 |  |  | ABCD | STR B MASS HIGH LIM | N |  | N | N
I545PD3504BK | 545ME201CG7 | HR | 523 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B DPT KP | N |  | N | N
I545T4500BK | 545ME201CG7 | HR | 525 |  | FLOAT32 | R | 1 | 0 | °C | 1000 |  |  | ABCD | STR B TT KP | N |  | N | N
I545P3500BK | 545ME201CG7 | HR | 527 |  | FLOAT32 | R | 1 | 0 | barg | 1000 |  |  | ABCD | STR B PT KP | N |  | N | N
I545PD1500AMD | 545ME201CG8 | HR | 529 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A DPT MODE(NOTE 2) | N |  | N | N
I545T4500AMD | 545ME201CG8 | HR | 530 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A TT MODE(NOTE 2) | N |  | N | N
I545P3500AMD | 545ME201CG8 | HR | 531 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A PT MODE(NOTE 2) | N |  | N | N
I545PD3504BMD | 545ME201CG8 | HR | 532 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B DPT MODE(NOTE 2) | N |  | N | N
I545T4500BMD | 545ME201CG8 | HR | 533 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B TT MODE(NOTE 2) | N |  | N | N
I545P3500BMD | 545ME201CG8 | HR | 534 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B PT MODE(NOTE 2) | N |  | N | N
I545F1501ASTS | 545ME201CG8 | HR | 535 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR A STATUS(NOTE 1) | N |  | N | N
I545F1501BSTS | 545ME201CG8 | HR | 536 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | STR B STATUS(NOTE 1) | N |  | N | N
I545A5500BT1 | 545ME201CG8 | HR | 537 |  | INT16 | R | 1 | 0 | S | 1000 |  |  | ABCD | GC ANALYSIS TIME | N |  | N | N
I545A5500BT2 | 545ME201CG8 | HR | 538 |  | INT16 | R | 1 | 0 | S | 1000 |  |  | ABCD | GC CYCLE TIME | N |  | N | N
I545A5500BCAL | 545ME201CG8 | HR | 539 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | GC CALIBR- ATION STATUS | N |  | N | N
I545A5500BRUN | 545ME201CG8 | HR | 540 |  | INT16 | R | 1 | 0 | S | 1000 |  |  | ABCD | GC RUNTIME | N |  | N | N
I545A5500BMD | 545ME201CG8 | HR | 541 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | GC MODE (NOTE 7) | N |  | N | N
I545F1501BSEQ | 545ME201CG8 | HR | 542 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM PRV SEQSTINDX(NOTE 4) | N |  | N | N
I545F1501BRUN | 545ME201CG8 | HR | 543 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM PRV RUNSTINDX(NOTE 5) | N |  | N | N
I545F1501BPSN | 545ME201CG8 | HR | 544 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM PRV STR NUMBER | N |  | N | N
I545F1501BPRR | 545ME201CG8 | HR | 545 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM REQUIRED RUN | N |  | N | N
I545F1501BPMR | 545ME201CG8 | HR | 546 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM MAXIMUM RUN | N |  | N | N
I545F1501BPSC | 545ME201CG8 | HR | 547 |  | INT16 | R | 1 | 0 |  | 1000 |  |  | ABCD | MM SEQ CTRL (NOTE 3) | N |  | N | N
545PD-1500AH | 545ME201CG10 | COIL | 551 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A DPT HI ALARM | N |  | N | N
545PD-1500AL | 545ME201CG10 | COIL | 551 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A DPT LO ALARM | N |  | N | N
545PD-1500AUR | 545ME201CG10 | COIL | 551 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A DPT URALARM | N |  | N | N
545PD-1500AOR | 545ME201CG10 | COIL | 551 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A DPT ORALARM | N |  | N | N
545T-4500AH | 545ME201CG10 | COIL | 551 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A TT HI ALARM | N |  | N | N
545T-4500AL | 545ME201CG10 | COIL | 551 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A TT LO ALARM | N |  | N | N
545T-4500AUR | 545ME201CG10 | COIL | 551 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A TT UR ALARM | N |  | N | N
545T-4500AOR | 545ME201CG10 | COIL | 551 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A TT OR ALARM | N |  | N | N
545P-3500AH | 545ME201CG10 | COIL | 551 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A PT HI ALARM | N |  | N | N
545P-3500AL | 545ME201CG10 | COIL | 551 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A PT LO ALARM | N |  | N | N
545P-3500AUR | 545ME201CG10 | COIL | 551 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A PT UR ALARM | N |  | N | N
545P-3500AOR | 545ME201CG10 | COIL | 551 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A PT OR ALARM | N |  | N | N
545F-1501ABH | 545ME201CG10 | COIL | 551 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A GSVOL FR HI ALARM | N |  | N | N
545F-1501ABL | 545ME201CG10 | COIL | 551 | 14 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A GSVOL FR LO ALARM | N |  | N | N
545F-1501AAH | 545ME201CG10 | COIL | 551 | 15 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A GUVOL FR HI ALARM | N |  | N | N
545F-1501AAL | 545ME201CG10 | COIL | 551 | 16 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A GUVOL FR LO ALARM | N |  | N | N
545F-1501ACH | 545ME201CG10 | COIL | 552 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A MASS FR HI ALARM | N |  | N | N
545F-1501ACL | 545ME201CG10 | COIL | 552 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR A MASS FR LO ALARM | N |  | N | N
545PD-3504BH | 545ME201CG11 | COIL | 553 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B DPT HI ALARM | N |  | N | N
545PD-3504BL | 545ME201CG11 | COIL | 553 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B DPT LO ALARM | N |  | N | N
545PD-3504BUR | 545ME201CG11 | COIL | 553 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B DPT URALARM | N |  | N | N
545PD-3504BOR | 545ME201CG11 | COIL | 553 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B DPT ORALARM | N |  | N | N
545T-4500BH | 545ME201CG11 | COIL | 553 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B TT HI ALARM | N |  | N | N
545T-4500BL | 545ME201CG11 | COIL | 553 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B TT LO ALARM | N |  | N | N
545T-4500BUR | 545ME201CG11 | COIL | 553 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B TT UR ALARM | N |  | N | N
545T-4500BOR | 545ME201CG11 | COIL | 553 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B TT OR ALARM | N |  | N | N
545P-3500BH | 545ME201CG11 | COIL | 553 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B PT HI ALARM | N |  | N | N
545P-3500BL | 545ME201CG11 | COIL | 553 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B PT LO ALARM | N |  | N | N
545P-3500BUR | 545ME201CG11 | COIL | 553 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B PT UR ALARM | N |  | N | N
545P-3500BOR | 545ME201CG11 | COIL | 553 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B PT OR ALARM | N |  | N | N
545F-1501BBH | 545ME201CG11 | COIL | 553 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B GSVOL FR HI ALARM | N |  | N | N
545F-1501BBL | 545ME201CG11 | COIL | 553 | 14 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B GSVOL FR LO ALARM | N |  | N | N
545F-1501BAH | 545ME201CG11 | COIL | 553 | 15 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B GUVOL FR HI ALARM | N |  | N | N
545F-1501BAL | 545ME201CG11 | COIL | 553 | 16 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B GUVOL FR LO ALARM | N |  | N | N
545F-1501BCH | 545ME201CG11 | COIL | 554 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | STR B MASS FR HI ALARM | N |  | N | N
545F-1501BCL | 545ME201CG11 | COIL | 554 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FR LO ALARM | N |  | N | N
545A-5500BMDV | 545ME201CG11 | COIL | 554 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | GC MOLE DEV ALARM | N |  | N | N
545A-5500BMH | 545ME201CG11 | COIL | 554 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | GC MOLE HI ALARM | N |  | N | N
545A-5500BML | 545ME201CG11 | COIL | 554 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | GC MOLE LO ALARM | N |  | N | N
545A-5500BRXF | 545ME201CG11 | COIL | 554 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | GC RX FAIL ALARM | N |  | N | N
545A-5500BRTO | 545ME201CG11 | COIL | 554 | 7 | BOOL | W | 1 | 0 |  | 1000 |  |  | CDAB | GC REP TIME OUT ALARM | N |  | N | N
545MOV7500OP | 545ME201CG12 | COIL | 555 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7500 OPN FEEDBACK | N |  | N | N
545MOV7500CL | 545ME201CG12 | COIL | 555 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7500 CLS FEEDBACK | N |  | N | N
545MOV7500LR | 545ME201CG12 | COIL | 555 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7500 LR FEEDBACK | N |  | N | N
545MOV-7500FLT | 545ME201CG12 | COIL | 555 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7500 FLT FEEDBACK | N |  | N | N
545MOV7500RDY | 545ME201CG12 | COIL | 555 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7500 RDY FEEDBACK | N |  | N | N
545MOV7501OP | 545ME201CG12 | COIL | 555 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501 OPN FEEDBACK | N |  | N | N
545MOV7501CL | 545ME201CG12 | COIL | 555 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501 CLS FEEDBACK | N |  | N | N
545MOV7501LR | 545ME201CG12 | COIL | 555 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501 LR FEEDBACK | N |  | N | N
545MOV-7501FLT | 545ME201CG12 | COIL | 555 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501 FLT FEEDBACK | N |  | N | N
545MOV7501RDY | 545ME201CG12 | COIL | 555 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501 RDY FEEDBACK | N |  | N | N
545MOV7502OP | 545ME201CG12 | COIL | 555 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7502 OPN FEEDBACK | N |  | N | N
545MOV7502CL | 545ME201CG12 | COIL | 555 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7502 CLS FEEDBACK | N |  | N | N
545MOV7502LR | 545ME201CG12 | COIL | 555 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7502 LR FEEDBACK | N |  | N | N
545MOV-7502FLT | 545ME201CG12 | COIL | 555 | 14 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7502 FLT FEEDBACK | N |  | N | N
545MOV7502RDY | 545ME201CG12 | COIL | 555 | 15 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7502 RDY FEEDBACK | N |  | N | N
545MOV7503OP | 545ME201CG12 | COIL | 555 | 16 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7503 OPN FEEDBACK | N |  | N | N
545MOV7503CL | 545ME201CG12 | COIL | 556 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7503 CLS FEEDBACK | N |  | N | N
545MOV7503LR | 545ME201CG12 | COIL | 556 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7503 LR FEEDBACK | N |  | N | N
545MOV-7503FLT | 545ME201CG12 | COIL | 556 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7503 FLT FEEDBACK | N |  | N | N
545MOV7503RDY | 545ME201CG12 | COIL | 556 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7503 RDY FEEDBACK | N |  | N | N
545MOV7504OP | 545ME201CG12 | COIL | 556 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7504 OPN FEEDBACK | N |  | N | N
545MOV7504CL | 545ME201CG12 | COIL | 556 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7504 CLS FEEDBACK | N |  | N | N
545MOV7504LR | 545ME201CG12 | COIL | 556 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7504 LR FEEDBACK | N |  | N | N
545MOV-7504FLT | 545ME201CG12 | COIL | 556 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7504 FLT FEEDBACK | N |  | N | N
545MOV7504RDY | 545ME201CG12 | COIL | 556 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7504 RDY FEEDBACK | N |  | N | N
545MOV7501BOP | 545ME201CG12 | COIL | 556 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501B OPN FEEDBACK | N |  | N | N
545MOV7501BCL | 545ME201CG12 | COIL | 556 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501B CLS FEEDBACK | N |  | N | N
545MOV7501BLR | 545ME201CG12 | COIL | 556 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501B LR FEEDBACK | N |  | N | N
545MOV-7501BFLT | 545ME201CG12 | COIL | 556 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501B FLT FEEDBACK | N |  | N | N
545MOV7501BRDY | 545ME201CG12 | COIL | 556 | 14 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7501B RDY FEEDBACK | N |  | N | N
545MOV7506OP | 545ME201CG12 | COIL | 556 | 15 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7506 OPN FEEDBACK | N |  | N | N
545MOV7506CL | 545ME201CG12 | COIL | 556 | 16 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7506 CLS FEEDBACK | N |  | N | N
545MOV7506LR | 545ME201CG12 | COIL | 557 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7506 LR FEEDBACK | N |  | N | N
545MOV-7506FLT | 545ME201CG12 | COIL | 557 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7506 FLT FEEDBACK | N |  | N | N
545MOV7506RDY | 545ME201CG12 | COIL | 557 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7506 RDY FEEDBACK | N |  | N | N
545MOV7507OP | 545ME201CG12 | COIL | 557 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7507 OPN FEEDBACK | N |  | N | N
545MOV7507CL | 545ME201CG12 | COIL | 557 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7507 CLS FEEDBACK | N |  | N | N
545MOV7507LR | 545ME201CG12 | COIL | 557 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7507 LR FEEDBACK | N |  | N | N
545MOV-7507FLT | 545ME201CG12 | COIL | 557 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7507 FLT FEEDBACK | N |  | N | N
545MOV7507RDY | 545ME201CG12 | COIL | 557 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7507 RDY FEEDBACK | N |  | N | N
545MOV7038OP | 545ME201CG12 | COIL | 557 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7038 OPN FEEDBACK | N |  | N | N
545MOV7038CL | 545ME201CG12 | COIL | 557 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7038 CLS FEEDBACK | N |  | N | N
545MOV7038LR | 545ME201CG12 | COIL | 557 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7038 LR FEEDBACK | N |  | N | N
545MOV-7038FLT | 545ME201CG12 | COIL | 557 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7038 FLT FEEDBACK | N |  | N | N
545MOV7038RDY | 545ME201CG12 | COIL | 557 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7038 RDY FEEDBACK | N |  | N | N
545MOV7039OP | 545ME201CG12 | COIL | 557 | 14 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7039 OPN FEEDBACK | N |  | N | N
545MOV7039CL | 545ME201CG12 | COIL | 557 | 15 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7039 CLS FEEDBACK | N |  | N | N
545MOV7039LR | 545ME201CG12 | COIL | 557 | 16 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7039 LR FEEDBACK | N |  | N | N
545MOV-7039FLT | 545ME201CG12 | COIL | 558 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7039 FLT FEEDBACK | N |  | N | N
545MOV7039RDY | 545ME201CG12 | COIL | 558 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MOV 7039 RDY FEEDBACK | N |  | N | N
545FQI-001A | 545ME201CG13 | COIL | 559 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 001 COLDSTART ALARM | N |  | N | N
545FQI-001B | 545ME201CG13 | COIL | 559 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 001 WARMSTART ALARM | N |  | N | N
545FQI-001C | 545ME201CG13 | COIL | 559 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 001 BATTFAIL ALARM | N |  | N | N
545FQI-001D | 545ME201CG13 | COIL | 559 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 001 TOT RESET ALARM | N |  | N | N
545FQI-001E | 545ME201CG13 | COIL | 559 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 001 TOT RO ALARM | N |  | N | N
545FQI-002A | 545ME201CG13 | COIL | 559 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 002 COLDSTART ALARM | N |  | N | N
545FQI-002B | 545ME201CG13 | COIL | 559 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 002 WARMSTART ALARM | N |  | N | N
545FQI-002C | 545ME201CG13 | COIL | 559 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 002 BATTFAIL ALARM | N |  | N | N
545FQI-002D | 545ME201CG13 | COIL | 559 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 002 TOT RESET ALARM | N |  | N | N
545FQI-002E | 545ME201CG13 | COIL | 559 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | FQI 002 TOT RO ALARM | N |  | N | N
545XA-101A | 545ME201CG14 | COIL | 561 | 1 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | PS 101A FAIL ALARM | N |  | N | N
545XA-101B | 545ME201CG14 | COIL | 561 | 2 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | PS 101B FAIL ALARM | N |  | N | N
545XA-101C | 545ME201CG14 | COIL | 561 | 3 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | TSTAT 101A HI ALARM | N |  | N | N
545XA-101D | 545ME201CG14 | COIL | 561 | 4 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | TSTAT 101B HI ALARM | N |  | N | N
545XA-101E | 545ME201CG14 | COIL | 561 | 5 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | AFS 101A FAIL ALARM | N |  | N | N
545XA-101F | 545ME201CG14 | COIL | 561 | 6 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | AFS 102A FAIL ALARM | N |  | N | N
545XA-101G | 545ME201CG14 | COIL | 561 | 7 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | AFS 101B FAIL ALARM | N |  | N | N
545XA-101H | 545ME201CG14 | COIL | 561 | 8 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | AFS 102B FAIL ALARM | N |  | N | N
545XA-101I | 545ME201CG14 | COIL | 561 | 9 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | ESW 101 FAIL ALARM | N |  | N | N
545XA-101J | 545ME201CG14 | COIL | 561 | 10 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | ESW 102 FAIL ALARM | N |  | N | N
545XA-101K | 545ME201CG14 | COIL | 561 | 11 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | MCB FAIL ALARM | N |  | N | N
545XA-101L | 545ME201CG14 | COIL | 561 | 12 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | SVC SW101 DSSTATUS | N |  | N | N
545XA-101M | 545ME201CG14 | COIL | 561 | 13 | BOOL | RW | 1 | 0 |  | 1000 |  |  | CDAB | SVC SW102 DSSTATUS | N |  | N | N